## Input
Room
walls
| Length [m] | A ext [m2] | window | door | A ext,net [m2]
West | 5 | 15 | 2 | 0 | 7.32
South | 7 | 21 | 1 | 1 | 12.12
East | 5 | 15 | 0 | 0 | 15
Unconditioned Room
walls
| Length [m] | A ext [m2] | door | A ext,net [m2]
South | 3 | 9 | 1 | 3.96
East | 5 | 15 | 0 | 15
H [m] |  | ε wall |  | V [m3]
3 |  | 0.6 |  | 105
Windows and doors
| W wind [m] | H wind [m] | A wind [m2]
window | 2.4 | 1.6 | 3.84
door | 2.4 | 2.1 | 5.04
Floor and ceiling
Room | A [m2] |  | Unconditioned Room | A [m2]
Floor | 35 |  | Floor | 15
Ceiling | 35 |  | Ceiling | 15
Climate data
Place | T int,winter [°C] | T ext,winter,des [°C] | climate zone | degree day
Genova | 20 | 0 | D | 1435
Month | T ext [°C] | p v,e [Pa] | T sky [°C] | ΔT sky [°C] | t [Ms]
January | 7.9 | 718 | -7.1667 | 15.0667 | 2.6784
Improvements
Mechanical ventilation? (y/n) |  | βk | q ve,des [m3/h]
n |  | 1 | 150
External wall insulation? (y/n) |  | Thickness [m] | Conductivity [W/m K]
n |  | 0.1 | 0.034
New windows? (y/n) |  | ε | Ug [W/m2K] | Uf [W/m2K]
n |  | 0.2 | 1.5 | 1
OUTPUT
Q h,tr [MJ] | 5565.5698
Q h,ve [MJ] | 562.464 |  | Q h,nd = (Q h,tr + Q h,ve) - η h,gn * (Q sol + Q int)
Q sol,w [MJ] | -1824.704
Q int [MJ] | -859.4742 |  | Q h,nd | 8621.2728 | [MJ]
η h,gn [MJ] | 0.92886 |  | Epi,env | 68.4228 | [kWh/m2year]

## Building structures
hr wall [W/m2 K] |  | ε roof | hr roof [W/m2 K]
2.782 |  | 0.5 | 2.3184
External Wall | Thickness [m] | Density [kg/m3] | Conductivity [W/m K] | R [m2K/W] |  | Internal Wall | Thickness [m] | Density [kg/m3] | Conductivity [W/m K] | R [m2K/W]
Rse |  |  |  | 0.04 |  | Rse |  |  |  | 0.25
External mortar | 0.03 | 2000 | 1.4 | 0.021429 |  | External mortar | 0.015 | 1800 | 0.9 | 0.016667
Perforated brick | 0.15 | 760 | 0.333 | 0.45045 |  | Perforated brick | 0.12 | 717 | 0.386 | 0.31088
Insulating 15 | 0.1 | 30 | 0.034 | 2.9412 |  | Internal mortar | 0.015 | 1800 | 0.9 | 0.016667
Mortar | 0.01 | 2000 | 1.4 | 0.0071429 |  | Rsi |  |  |  | 0.25
Perforated brick | 0.15 | 760 | 0.333 | 0.45045
Internal plaster | 0.02 | 1400 | 0.7 | 0.028571
External insulating | 0 | 30 | 0.034 | 0
Rsi |  |  |  | 0.25 |  |  |  |  | Rtot | 0.84421 | [m2K/W]
|  |  | Rtot | 4.1892 | [m2K/W] |  |  |  | Conductivity | 1.1845 | [W/m2K]
|  |  | Conductivity | 0.23871 | [W/m2K] |  |  |  | Surface | 15 | [m2]
|  |  | Surface | 19.44 | [m2] |  |  |  | Htr | 17.768 | [W/K]
|  |  | Htr | 4.6405 | [W/K]
[9 empty] | Equivalent resistance | 0.34421 | [m2K/W]
|  | Equivalent resistance |  | 0.9509 | [m2K/W] |  |  |  | Equivalent conductivity Ceq | 2.9052 | [W/m2K]
|  | Equivalent conductivity Ceq |  | 1.0516 | [W/m2K] |  |  |  | Leq | 0.15 | [m]
|  |  | Leq | 0.35 | [m] |  |  |  | Equivalent transmittance λeq | 0.43578 | [W/m K]
|  |  | Equivalent transmittance λeq | 0.36807 | [W/m K]
Floor | Thickness [m] | Density [kg/m3] | Conductivity [W/m K] | R [m2K/W] |  | Ceiling | Thickness [m] | Density [kg/m3] | Conductivity [W/m K] | R [m2K/W]
Rse |  |  |  | 0.04 |  | Rse |  |  |  | 0.04
External plaster | 0.02 | 1800 | 0.9 | 0.022222 |  | External floor (gres) | 0.015 | 1700 | 1.47 | 0.010204
Foundation | 0.16 | 900 | 0.56 | 0.28571 |  | Mortar | 0.02 | 2000 | 1.4 | 0.014286
Mortar | 0.02 | 2000 | 1.4 | 0.014286 |  | Screed | 0.06 | 1700 | 1.06 | 0.056604
Screed | 0.06 | 1700 | 1.06 | 0.056604 |  | Mortar | 0.02 | 2000 | 1.4 | 0.014286
Mortar | 0.02 | 2000 | 1.4 | 0.014286 |  | Foundation | 0.16 | 900 | 0.56 | 0.28571
Internal floor (gres) | 0.015 | 1700 | 1.47 | 0.010204 |  | Internal plaster | 0.02 | 1800 | 0.9 | 0.022222
Rsi |  |  |  | 0.25 |  | Rsi |  |  |  | 0.25
|  |  | Rtot | 0.69332 | [m2K/W] |  |  |  | Rtot | 0.69332 | [m2K/W]
|  |  | Conductivity | 1.4423 | [W/m2K] |  |  |  | Conductivity | 1.4423 | [W/m2K]
|  |  | Surface | 35 | [m2] |  |  |  | Surface | 35 | [m2]
|  |  | Htr | 50.482 | [W/K] |  |  |  | Htr | 50.482 | [W/K]
|  |  | Equivalent resistance | 0.33243 | [m2K/W] |  |  | Equivalent resistance |  | 0.33243 | [m2K/W]
|  |  | Equivalent conductivity Ceq | 3.0082 | [W/m2K] |  |  | Equivalent conductivity Ceq |  | 3.0082 | [W/m2K]
|  |  | Leq | 0.215 | [m] |  |  |  | Leq | 0.215 | [m]
|  |  | Equivalent transmittance λeq | 0.64676 | [W/m K] |  |  |  | Equivalent transmittance λeq | 0.64676 | [W/m K]
[6 empty] | Roof | Thickness [m] | Density [kg/m3] | Conductivity [W/m K] | R [m2K/W]
[6 empty] | Rse |  |  |  | 0.04
[6 empty] | Tiles | 0.01 | 1300 | 0.26 | 0.038462
[6 empty] | Air gap | 0.05 | 1 | 0.35 | 0.14286
[6 empty] | ISOVER SYNTO LIGHT lining | 0.001 | 200 | 10000 | 1e-07
[6 empty] | ISOVER E60 S panel | 0.06 | 30 | 0.035 | 1.7143
[6 empty] | BITUVER ALUVAPOR TENDER membrane | 0.002 | 1250 | 10000 | 2e-07
[6 empty] | Fir wood - perpendicular flux | 0.025 | 450 | 0.12 | 0.20833
[6 empty] | Rsi |  |  |  | 0.25
[9 empty] | Rtot | 2.3939 | [m2K/W]
[9 empty] | Conductivity | 0.41772 | [W/m2K]
[9 empty] | Surface | #REF! | [m2]
[9 empty] | Htr | #REF! | [W/K]
[8 empty] | Equivalent resistance |  | 1.9611 | [m2K/W]
[8 empty] | Equivalent conductivity Ceq |  | 0.50992 | [W/m2K]
[9 empty] | Leq | 0.097 | [m]
[9 empty] | Equivalent transmittance λeq | 0.049463 | [W/m K]
Beam | Thickness [m] | Density [kg/m3] | Conductivity [W/m K] | R [m2K/W] |  | Pillar | Thickness [m] | Density [kg/m3] | Conductivity [W/m K] | R [m2K/W]
Rse |  |  |  | 0.04 |  | Rse |  |  |  | 0.04
External plaster | 0.015 | 1800 | 0.9 | 0.016667 |  | External plaster | 0.03 | 1800 | 0.9 | 0.033333
Insulating | 0.1 | 37 | 0.034 | 2.9412 |  | Insulating | 0.1 | 30 | 0.034 | 2.9412
Pillar | 0.235 | 2400 | 1.91 | 0.12304 |  | Concrete | 0.24 | 2400 | 1.91 | 0.12565
Rsi |  |  |  | 0.13 |  | Internal plaster | 0.02 | 1400 | 0.7 | 0.028571
|  |  | Rtot | 3.2509 |  | Rsi |  |  |  | 0.25
|  |  | λtot | 0.30761 |  |  |  |  | Rtot | 3.4187
[9 empty] | λtot | 0.29251
|  |  | Equivalent resistance | 0.1397 | [m2K/W]
|  |  | Equivalent conductivity Ceq | 7.158 | [W/m2K] |  |  |  | Equivalent resistance | 3.1287 | [m2K/W]
|  |  | Leq | 0.25 | [m] |  |  |  | Equivalent conductivity Ceq | 0.31962 | [W/m2K]
|  |  | Equivalent λeq | 1.7895 | [W/m K] |  |  |  | Leq | 0.05 | [m]
[9 empty] | Equivalent λeq | 0.015981 | [W/m K]
Floor/ceiling | [5 empty] | Pillar in external corner
Adimensional transmittance U* | 1.2886 |  |  |  |  | Adimensional transmittance U* | 1.2254
Linear transmittance (external) [W/m K] | 0.3185 |  |  |  |  | λ eq [W/m K] | 0.36807
[6 empty] | Linear transmittance (external) [W/m K] | 0.079451
Linear transmittance (internal) [W/m K] | 1.003
[6 empty] | Linear transmittance (internal) [W/m K] | 0.32451
Internal wall on external wall
Lpin | 0.15
Upar | 0.23871
Linear transmittance (external) [W/m K] | 0
Linear transmittance (internal) [W/m K] | 0.042967
btr room - unconditioned room
Aiu surface [m2] | 15
Aue surface [m2] | 24
Hiu is the heat exchange [W/K] | 17.768
Hue is the heat exchange [W/K] | 5.729
btr | 0.24382

## Building windows
|  | ε window | hr window [W/m2 K]
|  | 0.89 | 4.1267
Window |  |  |  | Door
Rse | 0.04 | [m2K/W] |  | Rse | 0.04 | [m2K/W]
W | 2.4 | [m] |  | W | 2.4 | [m]
H | 1.6 | [m] |  | H | 2.1 | [m]
F | 0.08 | [m] |  | F | 0.08 | [m]
Ag | 3.1104 | [m2] |  | Ag | 4.1904 | [m2]
Af | 0.7296 | [m2] |  | Af | 0.8496 | [m2]
Ug | 3.1 | [W/m2K] |  | Ug | 3.1 | [W/m2K]
Uf | 2.4 | [W/m2K] |  | Uf | 2.4 | [W/m2K]
Ig | 10.08 | [m] |  | Ig | 12.08 | [m]
Ψg | 0.04 | [W/m K] |  | Ψg | 0.04 | [W/m K]
Rsi | 0.13 | [m2K/W] |  | Rsi | 0.13 | [m2K/W]
Uw | 3.072 | [W/m2K] |  | Uw | 3.0779 | [W/m2K]
Hd,w | 11.7965 | [W/K] |  | Hd,w | 15.5125 | [W/K]
Centre line window in insulated wall
Utel [W/m2 K] | 2.4
λ eq | 0.36807
ψ 1 [W/m K] | 0
ψ 2 [W/m K] | 0.097419
Linear transmittance (external) [W/m K] | 0.01353
Linear transmittance (internal) [W/m K] | 0.01353
𝑈_𝑊=(𝐴_𝑔 𝑈_𝑔+𝐴_𝑓 𝑈_𝑓+ 𝐼_𝑔 𝜓_𝑔)/(𝐴_𝑓+ 𝐴_𝑔 )

## Radiation
Rse [m2 K/W] | 0.04
Walls |  |  |  |  | Windows
hr wall [W/m2 K] | 2.782 |  |  |  | hr windows [W/m2 K] | 4.1267 |  | number | 3
Δ Tsky [°C] | 15.0667 |  |  |  | Δ Tsky [°C] | 15.0667 |  | Awind [m2] | 3.84
U wall [W/m2 K] | 0.23871 |  |  |  | U wind [W/m2 K] | 3.072
| A ext,net [m2] | Φ r,mn [W] | Fr | Φ r,mn*Fr [W] |  | Awind,tot [m2] | Φ r,mn [W] | Fr | Φ r,mn*Fr [W]
West | 7.32 | 2.9297 | 0.5 | 1.4648 |  | 11.52 | 88.0139 | 0.5 | 44.0069
South | 12.12 | 4.8507 | 0.5 | 2.4254
Door |  |  |  |  | Attic
hr door [W/m2 K] | 4.1267 |  | number | 1 | hr roof [W/m2 K] | 2.3184
Δ Tsky [°C] | 15.0667 |  | Awind [m2] | 5.04 | Δ Tsky [°C] | 15.0667
U door [W/m2 K] | 3.0779 |  |  |  | U roof [W/m2 K] | 0.41772
[5 empty] | btr | 0.7
| Awind,tot [m2] | Φ r,mn [W] | Fr | Φ r,mn*Fr [W] |  | Aroof [m2] | Φ r,mn [W] | Fr | Φ r,mn*Fr*(1-btr) [W]
| 5.04 | 38.5061 | 0.5 | 19.253 |  | 35 | 20.4274 | 0.5 | 7.7234
Unconditioned room |  |  |  |  | Unconditioned room door
hr wall [W/m2 K] | 2.782 |  |  |  | hr door [W/m2 K] | 4.1267 |  | number | 1
ΔTsky [°C] | 15.0667 |  |  |  | Δ Tsky [°C] | 15.0667 |  | Awind [m2] | 5.04
U wall [W/m2 K] | 0.23871 |  |  |  | U door [W/m2 K] | 3.0779
btr | 0.24382 |  |  |  | btr | 0.24382
| A ext,net [m2] | Φ r,mn [W] | Fr | Φ r,mn*Fr*(1-btr) [W] |  | A ext [m2] | Φ r,mn [W] | Fr | Φ r,mn*Fr*(1-btr) [W]
South | 3.96 | 1.5849 | 0.5 | 0.59923 | South | 5.04 | 38.5061 | 0.5 | 14.5588
East | 15 | 6.0034 | 0.5 | 2.2698
Qr [MJ] | 247.2202

## Transfer
btr
zone
ground | 0.45
attic | 0.7
unconditioned room | 0.24382
Thermal bridges
| corner | internal wall | windows | doors | floor | ceiling | floor unconditioned | ceiling unconditioned
n | 1 | 3 | 3 | 1 | 1 | 1 | 1 | 1
Linear transmittance (internal) [W/m K] | 0.32451 | 0.042967 | 0.01353 | 0.01353 | 1.003 | 1.003 | 1.003 | 1.003
Length [m] | 3 | 3 | 10.08 | 12.08 | 12 | 12 | 5 | 5
btr | [6 empty] | 0.24382 | 0.24382
H bridges [W/K] | 0.97352 | 0.38671 | 0.40916 | 0.16345 | 12.0358 | 12.0358 | 5.0149 | 5.0149
Q htr
Hd [W/K] |  |  | Htr,adj [W/K] | 171.731 |  | Hu [W/K]
walls | 22.4085 |  |  |  |  | unconditioned room | 4.3322
windows | 35.3894 |  | Hg [W/K] | 22.7169 |  | attic | 35.3374
door | 15.5125 |  |  |  |  | thermal bridges | 10.0298
thermal bridges | 26.0043
thermal bridges tot [W/K] | 36.0341
Htr,adj*ΔT*t [MJ] | 5565.5698
Q htr [MJ] | 5785.0539
Transfer thermal losses
Walls | 26.7406 | 323.5618 | 17.12%
Windows | 35.3894 | 428.2122 | 22.65%
Attic | 35.3374 | 427.5829 | 22.62%
Thermal Bridges | 36.0341 | 436.013 | 23.07%
Ground | 22.7169 | 274.8747 | 14.54%
| tot | 1890.2447
Thermal bridges
H [W/K]
walls | 1.3602 | 3.775%
windows and door | 0.57261 | 1.589%
floor | 17.0506 | 47.32%
ceiling | 17.0506 | 47.32%
tot | 36.0341

## Ventilation
Natural ventilation
Volume | 105 | [m3]
ρ a | 1.2 | [kg/m3]
C a | 1000 | [J/kg K]
n | 0.5 | [air changes/h]
q ve,0 | 0.014583 | [m3/s]
θ int,set,H | 20 | [°C]
θ e | 0 | [°C]
t | 744 | [h]
f ve,t | 0.6
q ve,mn | 0.00875 | [m3/s]
b ve | 1
H ve,adj | 10.5 | [W/K]
Q ve,adj | 562.464 | [MJ]
Mechanical ventilation
n50 | 7 | [h-1]
ε | 0.04
q' ve,x | 0.0081667 | [m3 /s]
q ve,f | 0.041667 | [m3 /s]
FC ve | 0.8
βk | 1
f | 15
q ve,sup (*) | 0.041667 | [m3 /s]
q ve,x | 0.00049142 | [m3 /s]
q ve,mn | 0.033825 | [m3 /s]
H ve,adj | 40.5897 | [W/K]
Q ve,adj | 2174.3093 | [MJ]
(*) = qve,f and qve,ext=0 if mechanical supply ventilation system; (*) = 0 and qve,ext=qve,f if mechanical extract ventilation system
𝐻_(𝑣𝑒,𝑎𝑑𝑗)= 𝜌_𝑎∙𝐶_𝑎∙∑2_𝐾▒𝑏_(𝑣𝑒,𝑘) 〖∙𝑞〗_(𝑣𝑒,𝑘,𝑚𝑛)
𝑞_(𝑣𝑒,0)=((𝑛 𝑉)/3600)
𝑞_(𝑣𝑒,𝑘,𝑚𝑛)=𝑞_(𝑣𝑒,0,) 𝑘×𝑓_(𝑣𝑒,𝑡,𝑘)
)k (1-βk) +)k βk
𝑞_(𝑣𝑒,𝑘,𝑚𝑛)=(¯(𝑞_(𝑣𝑒,0) )+¯(𝑞_(𝑣𝑒,𝑥)^′ ))k × (1-βk) +(𝑞_(𝑣𝑒,𝑓)×𝑏_𝑣𝑒×𝐹𝐶_𝑣𝑒+¯(𝑞_(𝑣𝑒,𝑥) ))k × βk
Daily average
〖𝑞′〗_(𝑣𝑒,𝑥)=𝑉 ×𝑛_50×ε/3600
¯(𝑞_(𝑣𝑒,𝑥) )=¯(𝑞_(𝑣𝑒,𝑥)^′ )/(1+𝑓/𝑒 [(𝑞_(𝑣𝑒,𝑠𝑢𝑝)−𝑞_(𝑣𝑒,𝑒𝑥𝑡))/(𝑉×𝑛_50/3600)]^2 )

## Q sol
I sol [MJ/m2] |  |  |  |  | f shut [MJ/m2]
| South | West/East | North |  |  | South | West/East | North
January | 118.1713 | 51.2731 | 19.5602 |  | January | 0.81 | 0.39 | 0
Room |  |  |  | Unconditioned room
Wall Orientation | S | W |  | Wall Orientation | S | E
Wall Surface [m2] | 21 | 15 |  | Wall Surface [m2] | 9 | 15
Windows Surface [m2] | 8.88 | 7.68 |  | Windows Surface [m2] | 5.04 | 0
Wall - Windows [m2] | 12.12 | 7.32 |  | Wall - Windows [m2] | 3.96 | 15
btr |  |  |  | btr | 0.24382 | 0.24382
g gl,n | 0.75 |  | Rse [m2 K/W] | 0.04
g_gl | 0.675 |  | time [Ms] | 2.6784
g_gl+sh/g_gl | 0.8
g_gl+sh | 0.54 |  | ε wall | 0.6
1-F f | 0.8 |  | ε windows | 0.89
Wall
| S | W | S uncond | E uncond
A sol [m2] | 0.069435 | 0.041936 | 0.022687 | 0.085935
Φ [W] | 8.2053 | 2.1502 | 2.6809 | 4.4062 | tot
Q sol [MJ] | 21.977 | 5.7591 | 5.4298 | 8.924 | 27.7361
Windows
| S | W
f sh,with | 0.81 | 0.39
F sh,gl | 0.838 | 0.922
A sol,w [m2] | 4.0184 | 3.8237
Φ sol,w [W] | 474.8569 | 196.0541 | tot
Q sol,w [MJ] | 1271.8567 | 525.1112 | 1796.9679
Q sol [MJ] | 1824.704

## Q int
Φ int
| room | uncondictioned
Af [m2] | 35 | 15
btr |  | 0.24382
Φ int [W] | 236.3025 | 111.8625
Q int
Q int [MJ] | room | uncondictioned | tot
Jan | 632.9126 | 226.5616 | 859.4742

## eta calculation
η_h,gn calculation
Q gn,winter | 2684.1782 | [MJ]
Q H,ht | 5785.2101 | [MJ]
γ h | 0.46397
H u | 72.4163 | [W/K]
H d | 63.9253 | [W/K]
H d,w | 35.3894 | [W/K]
H ve,adj | 10.5 | [W/K]
H m | 182.231 | [W/K]
C m | 125 | [kJ/m2K]
A d | 134.44 | [m2]
τ | 25.6161 | [h]
a h0 | 1
t h0 | 15 | [h]
a h | 2.7077
η h,gn | 0.92886
𝐻_𝑚=𝐻_𝑢+𝐻_𝑑+𝐻_(𝑑,𝑤)+𝐻_(𝑣𝑒,𝑎𝑑𝑗)
τ=𝐶_𝑚/𝐻_𝑚 ∗𝐴_𝑑
𝑎_ℎ= 𝑎_ℎ0+τ/τ_0