## Data
Case Study: Determination of the optimal thickness of insulation
Month |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Avg. Ext. Temperature | °C | 1.6568 | 3.5019 | 8.3577 | 11.6343 | 16.2502 | 20.2629 | 22.7979 | 22.1574 | 18.0945 | 12.6812 | 6.5701 | 2.4104
Avg. Wind Velocity | km/h | 30 | 30 | 20 | 15 | 10 | 5 | 5 | 5 | 10 | 15 | 20 | 30
Thermal Conductivity
Stainless Steel | W/(mK) | 1: 15
Pipe Data
Twater | °C | 1: 90
Diameter | cm | 1: 30
Thickness | cm | 1: 0.3
Total length | km | bar: 1

## Thermal Optimization
External convection coefficient calculation
number of circuits |  | 10 | [10 empty] | Parallel Flow Correlation
Length of one circuit | m | 100
Average Properties of Air @ 300 K | [12 empty] | Cross Flow Correlations
k | W/(mK) | 0.0263 |  | Pr |  | 0.707
cp | kJ/(kgK) | 1.007 |  | ni | m^2/s | 1.589e-05
Month | Unit | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Wind Velocity | m/s | 8.3333 | 8.3333 | 5.5556 | 4.1667 | 2.7778 | 1.3889 | 1.3889 | 1.3889 | 2.7778 | 4.1667 | 5.5556 | 8.3333
Parallel Flow: |  | January | February | March | April | May | June | July | August | September | October | Novmeber | December
Re | n.a. | 52443885.043 | 52443885.043 | 34962590.0287 | 26221942.5215 | 17481295.0143 | 8740647.5072 | 8740647.5072 | 8740647.5072 | 17481295.0143 | 26221942.5215 | 34962590.0287 | 52443885.043
Flow type |  | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent | Turbulent
Nu | n.a. | 49404.2238 | 49404.2238 | 35718.3241 | 28375.2753 | 20514.7901 | 11782.6528 | 11782.6528 | 11782.6528 | 20514.7901 | 28375.2753 | 35718.3241 | 49404.2238
Avg. Heat Transfer Coeff. | W/(m^2K) | 12.9933 | 12.9933 | 9.3939 | 7.4627 | 5.3954 | 3.0988 | 3.0988 | 3.0988 | 5.3954 | 7.4627 | 9.3939 | 12.9933
Cross Flow:
Re |  | 160478.2882 | 160478.2882 | 106985.5255 | 80239.1441 | 53492.7627 | 26746.3814 | 26746.3814 | 26746.3814 | 53492.7627 | 80239.1441 | 106985.5255 | 160478.2882
Nu |  | 372.8467 | 372.8467 | 269.0152 | 213.4033 | 153.9741 | 88.1289 | 88.1289 | 88.1289 | 153.9741 | 213.4033 | 269.0152 | 372.8467
Avg. Heat Transfer Coeff. | W/(m^2K) | 32.0453 | 32.0453 | 23.1212 | 18.3415 | 13.2337 | 7.5745 | 7.5745 | 7.5745 | 13.2337 | 18.3415 | 23.1212 | 32.0453
Avg. Cross/Parallel Heat Tran. Coeff. | W/(m^2K) | 22.5193 | 22.5193 | 16.2576 | 12.9021 | 9.3146 | 5.3367 | 5.3367 | 5.3367 | 9.3146 | 12.9021 | 16.2576 | 22.5193
Thermal Resistance Calculation
Internal Pipe Radius | cm | January: 15
External Pipe Radius | cm | January: 15.3
Insulator Thickness | cm | January: 5.5185; February: Initial Value
Total External Radius | cm | January: 20.8185
Insulator Conductivity | W/(mK) | January: 0.06
Thermal Resistances
Pipe | K/W | January: 2.1012e-06
Insulator | K/W | January: 0.00817
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
External Pipe Surface Ins. | m^2 | 130.8029 | 130.8029 | 130.8029 | 130.8029 | 130.8029 | 130.8029 | 130.8029 | 130.8029 | 130.8029 | 130.8029 | 130.8029 | 130.8029
External Pipe Surface No Ins. | m^2 | 96.1299 | 96.1299 | 96.1299 | 96.1299 | 96.1299 | 96.1299 | 96.1299 | 96.1299 | 96.1299 | 96.1299 | 96.1299 | 96.1299
Convective Resistance Ins. | K/W | 0.00033949 | 0.00033949 | 0.00047025 | 0.00059255 | 0.00082077 | 0.0014326 | 0.0014326 | 0.0014326 | 0.00082077 | 0.00059255 | 0.00047025 | 0.00033949
Convective Resistance No Ins. | K/W | 0.00046194 | 0.00046194 | 0.00063986 | 0.00080627 | 0.0011168 | 0.0019493 | 0.0019493 | 0.0019493 | 0.0011168 | 0.00080627 | 0.00063986 | 0.00046194
Totale Resistance | K/W | 0.0085116 | 0.0085116 | 0.0086423 | 0.0087646 | 0.0089928 | 0.0096046 | 0.0096046 | 0.0096046 | 0.0089928 | 0.0087646 | 0.0086423 | 0.0085116
Totale Resistance No Ins. | K/W | 0.00046404 | 0.00046404 | 0.00064196 | 0.00080837 | 0.0011189 | 0.0019514 | 0.0019514 | 0.0019514 | 0.0011189 | 0.00080837 | 0.00064196 | 0.00046404
Energy Waste Calculation
Month |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Total
External Temperature | °C | 1.6568 | 3.5019 | 8.3577 | 11.6343 | 16.2502 | 20.2629 | 22.7979 | 22.1574 | 18.0945 | 12.6812 | 6.5701 | 2.4104
Internal Pipe Surf. Temp. | °C | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
Total Resistance Insulator | K/W | 0.0085116 | 0.0085116 | 0.0086423 | 0.0087646 | 0.0089928 | 0.0096046 | 0.0096046 | 0.0096046 | 0.0089928 | 0.0087646 | 0.0086423 | 0.0085116
Total Resistance No Insulator | K/W | 0.00046404 | 0.00046404 | 0.00064196 | 0.00080837 | 0.0011189 | 0.0019514 | 0.0019514 | 0.0019514 | 0.0011189 | 0.00080837 | 0.00064196 | 0.00046404
Heat Power per Circuit Ins. | kW | 10.3792 | 10.1624 | 9.4468 | 8.9411 | 8.201 | 7.2608 | 6.9968 | 7.0635 | 7.9959 | 8.8217 | 9.6537 | 10.2907
Heat Power per Circuit No Ins. | kW | 190.3777 | 186.4015 | 127.1762 | 96.9427 | 65.9121 | 35.7375 | 34.4384 | 34.7666 | 64.2638 | 95.6476 | 129.9609 | 188.7537
n. days per month |  | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
hour per month |  | 744 | 672 | 744 | 720 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744
Energy Dissipation per Circuit | kWh | 7722.1291 | 6829.1541 | 7028.4248 | 6437.624 | 6101.5085 | 5227.7604 | 5205.6497 | 5255.2706 | 5757.0196 | 6563.3469 | 6950.6323 | 7656.2577 | 76734.7778
Energy Dissipation per Circuit No Ins | kWh | 141640.9727 | 125261.8316 | 94619.0894 | 69798.7089 | 49038.6215 | 25730.9825 | 25622.1536 | 25866.3871 | 46269.919 | 71161.8352 | 93571.8198 | 140432.7454 | 909015.0668
Cost Data
Cost of Insulator | €/cm/m^2 | 1: 10
Useful life of Ins. | Years | 1: 25
Total Invest Cost | € | 1: 72184.2025
|  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
NG Price Increase | % |  | 2.933% | 3.012% | 2.922% | 2.999% | 2.992% | 2.986% | 3.059% | 2.972% | 3.044% | 3.036% | 3.028% | 3.02% | 3.013% | 3.08% | 3.071% | 3.062% | 3.053% | 3.053% | 3.053% | 3.053% | 3.053% | 3.053% | 3.053% | 3.053% | 3.053%
Avg. Heat Price | €/kWht | 0.1296 | 0.1334 | 0.13742 | 0.14143 | 0.14568 | 0.15003 | 0.15451 | 0.15924 | 0.16397 | 0.16897 | 0.1741 | 0.17937 | 0.18478 | 0.19035 | 0.19621 | 0.20224 | 0.20843 | 0.21479 | 0.22135 | 0.22811 | 0.23507 | 0.24225 | 0.24965 | 0.25727 | 0.26512 | 0.27322
Investment Valuation
Discount Rate | 10%
Total Investment Cost | 72184.2025 | bar: 72184.2025 2016
|  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Energy Savings | kWh |  | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891 | 832280.2891
Cash Flow | € |  | 111026.9467 | 114370.7708 | 117712.3987 | 121242.7258 | 124870.851 | 128599.2741 | 132533.6123 | 136472.4365 | 140626.6903 | 144896.1952 | 149283.8995 | 153792.8235 | 158426.0608 | 163305.1601 | 168319.7228 | 173473.2159 | 178769.1908 | 184226.8469 | 189851.12 | 195647.097 | 201620.0197 | 207775.2902 | 214118.4753 | 220655.3119 | 227391.712
NPV | € | € 2016: 1208791.041
Insulator Cost €/cm/m^2)
|  | NPV (€) | 1208791.041 | 5 | 8 | 10 | 15 | 20
|  |  | 1 | 976838.0069 | 973765.6199 | 971717.3619 | 966596.7169 | 961476.0719
|  |  | 2 | 1131052.2379 | 1124530.4839 | 1120182.6479 | 1109313.0579 | 1098443.4679
|  |  | 3 | 1192499.338 | 1182151.237 | 1175252.503 | 1158005.668 | 1140758.833
|  |  | 4 | 1223234.9055 | 1208683.4775 | 1198982.5255 | 1174730.1455 | 1150477.7655
|  | Ins. Thickness | 5 | 1239710.2531 | 1220578.5181 | 1207824.0281 | 1175937.8031 | 1144051.5781
|  | (cm) | 6 | 1248211.2541 | 1224122.2321 | 1208062.8841 | 1167914.5141 | 1127766.1441
|  |  | 7 | 1251668.0102 | 1222244.7212 | 1202629.1952 | 1153590.3802 | 1104551.5652
|  |  | 8 | 1251632.7904 | 1216498.2544 | 1193075.2304 | 1134517.6704 | 1075960.1104
|  |  | 9 | 1249005.4603 | 1207782.6973 | 1180300.8553 | 1111596.2503 | 1042891.6453
|  |  | 10 | 1244343.9389 | 1196655.9689 | 1164863.9889 | 1085384.0389 | 1005904.0889